## Slide 1: An Energy-Harvesting Sensor Architecture and Toolkit for Building Monitoring and Event Detection
Brad Campbell and Prabal Dutta
University of Michigan
BuildSys’14 – November 6, 2014

## Slide 2: Buildings must become more efficient while maintaining occupant comfort
Buildings represent 39% of the energy use in the U.S. and we spend 90% of our time indoors.
Goals: reduce energy consumption improve occupant comfort

## Slide 3: BuildSys work targets the energy and comfort issues
Energy
Comfort
PresenceSense [BuildSys’14]
BlueSentinel [BuildSys’14]
Fixture Assignment [BuildSys’14]
MCC HVAC Fault Detection [BuildSys’14]
Occupancy Context
Sensing [BuildSys’14]
ZonePAC
[BuildSys’13]
HVAC Predictive Control [BuildSys’13]
Circulo [BuildSys’13]
Retail Energy Analysis [BuildSys’13]
Energy-Water Nexus [BuildSys’13]
Models for Diagnosing Abnormal Energy Usage [BuildSys’13]
Carrying My Environment [BuildSys’13]
Room-Level
Thermal Control [BuildSys’13]
Observation
Models
Datasets
Algorithms
Sensors

## Slide 4: These sensors are often not the focus and hard to scale to building-size
Current sensors
One-off designs
Tailored to a particular need
Used to demonstrate model
Ideal
Reusable and reconfigurable sensors
Easily scale to building-wide deployment

## Slide 5: These sensors must be installable and scalable
 |  | Power | 
 |  | AC Mains | Battery
Size | Large |  | 
 | Small |  | 
 |  | Power |  | 
 |  | AC Mains | Battery | Energy- Harvesting
Size | Large |  |  | 
 | Small |  |  | 
Main limiting factors: size and power
Installable Scalable
N/A
Installable Scalable
Installable Scalable
Installable Scalable
Installable Scalable
Small, energy-harvesting sensors

## Slide 6: Energy-harvesting sensors exist, but are typically single-purpose
DoubleDip
Water metering
Paul Martin, Zainul Charbiwala, and Mani Srivastava. 2012. DoubleDip: leveraging thermoelectric harvesting for low power monitoring of sporadic water use. SenSys '12
Trinity
Airflow metering
Feng Li, Tianyu Xiang, Zicheng Chi, Jun Luo, Lihua Tang, Liya Zhao, and Yaowen Yang. 2013. Powering indoor sensing with airflows: a trinity of energy harvesting, synchronous duty-cycling, and sensing. SenSys '13

## Slide 7: An architecture for energy-harvesting sensors can ease development
Energy-Harvesting Power Supply
Trigger
Sensor
Data Communication
Log or transmit data wirelessly
Optional dedicated sensor
Wake-up mechanism
Harvester for any energy source

## Slide 8: The energy-harvesting power supply defines many operational parameters
Architecture is harvester agnostic
  Solar, piezoelectric, thermoelectric, electromagnetic, etc.
Defines maximum duty cycle
  Intermittent versus continuous
Energy-Harvesting Power Supply
Trigger
Sensor
Data Communication
Energy-Harvesting Power Supply
Trigger
Shutdown
VCC
Interface:

## Slide 9: The trigger layer masks the intermittency inherit in energy-harvesting
Key: just need sufficient energy when an event occurs
Energy-Harvesting Power Supply
Trigger
Sensor
Data Communication
Energy Harvested
Time
activation threshold
Variable, unpredictable harvesting
Waiting for event
triggered event occurs
Triggers:
Periodic – regular intervals
Opportunistic – when sufficient energy
Event based – external event occurs

## Slide 10: The optional sensing layer allows for common sensors to be sampled
Ideal: Sensors with short power-on to valid sample time
Trigger may be sufficient
  To determine when energy is being harvested
  To detect an event
Energy-Harvesting Power Supply
Trigger
Sensor
Data Communication

## Slide 11: The data communication layer stores or forwards data
Energy-Harvesting Power Supply
Trigger
Sensor
Data Communication
Network connectivity provided by gateways or other nodes
Possible offloading via Bluetooth to phones
Highly reusable
Single hop communication
Local logging
device collection

## Slide 12: Revisiting the prior energy-harvesting designs
DoubleDip
Power supply: thermoelectric generator
Trigger: event based, spike on harvester
Sensor: accelerometer
Data communication: immediate and batching
Paul Martin, Zainul Charbiwala, and Mani Srivastava. 2012. DoubleDip: leveraging thermoelectric harvesting for low power monitoring of sporadic water use. SenSys '12
Trinity
Power supply: piezoelectric
Trigger: periodic
Sensor: piezoelectric airflow
Data communication: immediate
Feng Li, Tianyu Xiang, Zicheng Chi, Jun Luo, Lihua Tang, Liya Zhao, and Yaowen Yang. 2013. Powering indoor sensing with airflows: a trinity of energy harvesting, synchronous duty-cycling, and sensing. SenSys '13

## Slide 13: To validate this architecture, we implemented three new sensors with reusable components
Buzz
Breeze
BigBen

## Slide 14: Power Supply: Indoor photovoltaic based harvester
Shared harvester that is useful for indoor sensing
When people are around, the lights are typically on
Provides trigger and shutdown interface
5.8 cm2
In reasonable lighting, charged every two minutes
3.8 cm
1.5 cm

## Slide 15: Buzz: A vibration sensor
Trigger: Piezoelectric event detector
Sensor: Event-based from trigger
Communication: Packet on event detection
Door event detection:
60% detection rate

## Slide 16: Breeze: An airflow sensor
Trigger: Opportunistic when energy available
Sensor: MEMS airflow meter
Communication: Packet on sample
Airflow detection:
Can detect air vent state changes

## Slide 17: BigBen: A local-logging light sensor
Trigger: Opportunistic when energy available
Sensor: None
Communication: Log light state changes in FRAM
Additional: RTC with small battery
Light state detection:
Light state detection shifted 40 seconds

## Slide 18: Conclusion: Architecture for creating energy-harvesting sensors
Leverage energy-harvesting to eliminate sensor maintenance
Mask intermittency by waiting for a trigger
Compose hardware layers to build a range of sensors
Address the sensor scaling issue

## Slide 19: Questions?
Brad Campbell
bradjc@umich.edu
github.com/lab11
University of Michigan