## Slide 1: Gemini: A Non-Invasive, Energy-Harvesting True Power Meter
Brad Campbell and Prabal Dutta
University of Michigan
RTSS’14 – December 5, 2014

## Slide 2: Buildings are significant consumers of electricity worldwide
Source: Natural Resources Defense Council, “Constructing Change: Accelerating Energy Efficiency in India’s Buildings Market”
Source: JRC, “Electricity Consumption and Efficiency Trends in European Union”
55.3%
Source: NIST, “Measurement Science Roadmap for Zero-Net Energy Buildings”

## Slide 3: But we don’t know where the electricity goes inside of the building
“To properly direct [building efficiency] efforts, planners must understand where energy…is consumed.”
US National Science and Technology Council Committee on Technology, Oct 2011
“Technological areas requiring further development include sensing and measurement technologies.”
US National Science Board August 2009
“However, sub-metered energy use data are not available for many buildings, often due to the high cost of metering and gathering data.”
US Department of Energy Building Technologies Office
Notes: Make two slides

## Slide 4: Gemini: A true power meter to address this issue
Circuit panel level energy-harvesting meter that measures true power
Current Meter
Voltage Monitor
Two devices work together to calculate power

## Slide 5: How can we determine the electricity breakdown?
Meter every device
?
High installation cost
Configuration
Single watch point solutions
Extensive calibration
Scale issues
Meter at the circuit level
Defined sense points
Reasonable load fidelity

## Slide 6: End goal: Measure true power P(t)=I(t)*V(t)
Voltage
Current
Power

## Slide 7: Existing commercial meters are expensive and hard to install
Installation complexity
  Labor cost
  Infrastructure upgrade
Meter cost
  Easily >$1000
Highly accurate
Metering
Circuits
Metering
Circuits
Notes: Explain the meters.

## Slide 8: Research solutions address cost, installation, and size issues
Magnetometer1
Interference
Current Transformer Energy-Harvester (Monjolo)3
Calibration and cross-talk issues
Not actually measuring true power
Accuracy issues
Piezoelectromagnetic (PEM)2
1Patel, et. al, “The Design and Evaluation of an End-User-Deployable, Whole House, Contactless Power Consumption Sensor” CHI’10
2Xu, et. al, “Stick-On Piezoelectromagnetic AC Current Monitoring of Circuit Breaker Panels” Sensors’13
3DeBruin, et. al, “Monjolo: An Energy-Harvesting Energy Metering Architecture” SenSys’13
Notes: Add citations. Again explain each device clearer. Add device type to monjolo. Swap pem and mag.

## Slide 9: Not measuring true power leads to errors in non-unity power factor loads
Many loads have power factors < 1
Notes: If you do not calculate true power . If not unity power factor, that is votlage and current arent sinusoids or are phase shifted then error high

## Slide 10: We are missing the sweet spot of panel meter designs
`` | Install Cost | Unit Cost | Size | Online Calib. | Acc. | Cross Sensitivity | True Power | Update Rate
Commercial |  |  |  |  |  |  |  | 
Magnetometer |  |  |  |  |  |  |  | 
PEM |  |  |  |  |  |  |  | 
Monjolo |  |  |  |  |  |  |  | 
Clear cost vs. performance trade-offs
Cost
Performance
Notes: Greener green

## Slide 11: Panel power meter wishlist
Simple installation
  Small devices – fit in existing panels
  Retrofit
Low unit cost
  DOE Wireless Metering Challenge: $100
Revenue grade accuracy not required
  2-5% error is fine
No deployment-time calibration procedure
Notes: Crisp description of reqs.

## Slide 12: Gemini: energy-harvesting true power meter
5 cm
Current Meter
Calculates true power by distributing current and voltage acquisition.
Voltage Monitor
Non-contact
Calculates true power
Energy-harvesting
Virtualized Voltage
Notes: Accurate relative timing is key
Overview image

## Slide 13: Virtualizing the voltage channel
VAC<A,φ>
Many current sensors that synthesize the voltage channel locally
Voltage Monitor
A
φ
Current Meter
Few meters with access to voltage channel
Notes: ----- Meeting Notes (11/26/14 14:10) -----
compute reconstruction error for the

## Slide 14: Voltage waveforms can be represented by one or a few Fourier Coefficients
Voltage
Current
Notes: Harmonic distortion is much smaller on the voltage waveform than for the current waveform.
----- Meeting Notes (11/26/14 14:10) -----
compute reconstruction error for the

## Slide 15: Key: properly phase-aligning the current and voltage waveforms
Voltage Monitor
Current Meter
V?
V?
A
SFD
Δt
A, Δt
SFD
Δt
A single packet provides time synchronization
Do not need time sync protocols
Δt

## Slide 16: The current sensor’s energy-harvesting power supply limits its computational runtime
Duty cycle of 0.2% (load at 5 W)
1. Request Voltage
2. Sample Current
3. Receive Voltage
4. Calculate Power
5. Store Result
3 mJ
1
2
3
4
5
Notes: Add labels between lines and events

## Slide 17: Results: average error 8.7%, average absolute error: 2.2 W
Gemini
Ground Truth
Percent Error

## Slide 18: Timing errors between voltage and current have large effects on error
Notes: Explain expirement better. Artificially introduce error. Highlight points.
Combining values measured at distinct locations is not necessarily new, but timing matters here (sub ms)

## Slide 19: The effect of measuring voltage at a different location is minimal
φ
VR=IR
VL=IZL
V=IZ
1.7° (0.08 ms) voltage phase difference between the two loads
Impedance of the loads:
Voltage triangle:
Calculate phase offset:
Notes: 3% error for fridge
30 meters of 14 gauge wire = 0.25 ohms

## Slide 20: Approximating voltage with a single Fourier coefficient results in less than 2% error
Power calculation error using synthesized voltage

## Slide 21: The current sensor must use the correct voltage channel in its calculations
Buildings typically have three phase power (three voltage channels offset by 120°).
How does the sensor choose the correct voltage channel?
Heuristic: Try all three voltage phases and choose the largest value.
Correct
±180°
120°
240°
Notes: Automatic mapping removes the need for human configuration – which is wrong sometimes
Question: how do we know which is the correct voltage phase?

## Slide 22: Revisiting the matrix of panel meter designs
`` | Install Cost | Unit Cost | Size | Online Calib. | Acc. | Cross Sensitivity | True Power | Update Rate
CT Based |  |  |  |  |  |  |  | 
Magnetometer |  |  |  |  |  |  |  | 
PEM |  |  |  |  |  |  |  | 
Monjolo |  |  |  |  |  |  |  | 
Gemini |  |  |  |  |  |  |  | Load Proportional
Gemini Limitations
Sample rate
  Possibility: add a single daisy chained wire for power to each current transformer
Detecting broken nodes
  When load is off harvesting stops and updates stop
  Possibly look at historical trends to distinguish

## Slide 23: Gemini is an accurate true power meter
Installable
  Small, independent current transformers
Accurate
  Virtualized voltage allows for sample-by-sample power calculations

## Slide 24: Questions?
Brad Campbell
bradjc@umich.edu
http://bradcampbell.com
http://lab11.eecs.umich.edu
University of Michigan

## Slide 25: Power meter design
Energy-harvesting power supply
Measurement and communication
Uses multiple Current Transformers
  For harvesting and measurement
  Working on a design for multiplexing a single
Notes: Label as current meter. Break down and explain the pieces. Green box could be replaced by wires or battery.

## Slide 26: Cost