## Slide 1: From Energy Audits to Monitoring Megawatt Loads: A Flexible and Deployable Power Metering System
Brad Campbell, Ye-sheng Kuo, Prabal Dutta
IoTDI’18

## Slide 2: We need submetering!
“However, sub-metered energy use data are not available for many buildings, often due to the high cost of metering and gathering data.”
US Department of Energy Building Technologies Office
Buildings
Maintenance
Money Saving

## Slide 3: Does anyone actually want new submeters?
System Integrators
“Submetering? That’s a solved problem.”
“Johnson Controls and Siemens sell solutions.”
Potential Users
“I can’t guarantee a ROI.”
“Continuous monitoring is too expensive.”
“I can’t schedule the downtime.”
“I would love to see how my equipment is performing.”
?

## Slide 4: Current submetering options have numerous drawbacks
Meter Cost
Installation Complexity
Accuracy
Connectivity
Limited Use Cases
Calibration

## Slide 5: Triumvi integrates several techniques to address these issues
Standalone
Accurate
Upgradeable
Scalable
Configurable
Flexible
Monjolo [SenSys’13]
Gemini [RTSS’14]

## Slide 6: Standalone operation requires a power source, the current channel, and the voltage channel
Power Source
Current Channel
Tap into breakers
External outlet
Battery
Energy-harvesting
Hall effect sensor
Additional current transformer
Reuse current transformer
VCC
LTC3588

## Slide 7: Sharing the current transformer requires carefully switching between modes

## Slide 8: Standalone operation requires a power source, the current channel, and the voltage channel
Power Source
Current Channel
Voltage Channel
Tap into breakers
External outlet
Battery
Energy-harvesting
Hall effect sensor
Additional current transformer
Reuse current transformer
Direct contact
Wireless sync
Capacitive coupling
VCC
LTC3588

## Slide 9: Without calibration, detecting voltage phase is accurate
Voltage amplitude, however, is not
Graph from paper on wire position versus error

## Slide 10: Access to the voltage channel enables higher accuracy than current-only approaches (PF=0.85)
Graphs from paper on error with loads of differencing power factor
Triumvi
Triumvi without voltage
Voltage uncertainty
Triumvi
Pressac CT

## Slide 11: Energy-harvesting + current transformer + capacitive voltage coupling = accurate, standalone energy meter
Some sort of recap slide
Energy-Harvesting
Measurement
Transmission
802.15.4

## Slide 12: Triumvi can sense a range of loads accurately (6.2% RMS error)
3 graphs from paper
“Home”
“Office”
Servers

## Slide 13: Triumvi nodes can share charge to help “struggling” circuits
And they can synchronize their sampling for three phase loads
1
2
3
Shared bus
Wired NOR
All nodes sample simultaneously
600 W Circuit
60 W
Circuit

## Slide 14: Triumvi can adapt to different deployment scenarios
Current Waveform Analysis
Reported by Triumvi
Large Loads
Rated for 1000 A
Local Interval Data
Time Req
Current Time
RTC
FRAM
Timestamped measurements
Reliable Sampling
DC Power Supply
Daisy-chained power

## Slide 15: So deploy we did! Quick “energy audits” in an apartment.
“Deploy on Monday, inspect on Wednesday”

## Slide 16: Longer term measurements in a house
One day breakdown
1,693,966 measurements in 1 month

## Slide 17: Monitoring large (~50 kW) water pumps
4,046,215 measurements
88.4% of the samples successfully received
Packet interval: 90th percentile is 2.46 seconds
Consecutively dropped packets: 99.9th percentile is five dropped packets

## Slide 18: Triumvi: a flexible energy metering platform
Standalone: energy-harvesting + current sensing + voltage phase sensing
Flexible: multiple operating modes, large loads, synchronized sampling, charge sharing
Deployable: supports multiple deployment scenarios
Brad Campbell
bradjc@virginia.edu
@bradjc5